NOTICE OF INTENT

Department of Natural Resources

Office of Conservation

Pipeline Safety
(LAC 43:XIII:Chapters 3-61 and LAC 33:V.Chapter 304)

The Department of Natural Resources, Office of Conservation proposes to amend LAC 43:XIII and LAC 33 Part V Subpart 3 in accordance with the provisions of the Administrative Procedure Act, R.S. 49:950 et seq., and pursuant to the power delegated under the laws of the state of Louisiana.

The proposed rule changes are required as a part of the Department of Natural Resources certification agreement with the US Department of Transportation and are intended to adopt existing federal regulations as state regulations.

Title 43

NATURAL RESOURCES

Subpart 2.  Transportation of Natural Gas and Other Gas by Pipeline 
[49 CFR Part 191]

- Chapter 3.  Annual Reports, Incident Reports and Safety Related Condition Reports [49 CFR Part 191]

§303.	Definitions 
[49 CFR 191.3]

* * *

Incident—any of the following events:

a.	an event that involves a release of gas from a pipeline, gas from an underground natural gas storage facility (UNGSF), liquefied natural gas, liquefied petroleum gas, refrigerant gas, or gas from an LNG facility, and that results in one or more of the following consequences:

i.	a death, or personal injury necessitating in-patient hospitalization;

ii.	estimated property damage of $50,000 or more, including loss to the operator and others, or both, but excluding cost of gas lost; estimated property damage of $122,000 or more, including loss to the operator and others, or both, but excluding the cost of gas lost. For adjustments for inflation observed in calendar year 2021 onwards, changes to the reporting threshold will be posted on PHMSA’s website. These changes will be determined in accordance with the procedures in Chapter 4, Appendix A to Subpart 2.

iii.	unintentional estimated gas loss of three million cubic feet or more;

* * *

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 11:255 (March 1985), amended LR 18:854 (August 1992), LR 20:442 (April 1994), LR 27:1536 (September 2001), LR 30:1221 (June 2004), LR 33:473 (March 2007), LR 38:110 (January 2012), LR 44:1032 (June 2018), LR 45:66 (January 2019), LR 46:1575 (November 2020), LR.

§311.	Distribution System: Annual Report 
[49 CFR 191.11]

- …

- B.	Not Required. The annual report requirement in this Section does not apply to a master meter system or to a petroleum gas system that serves fewer than 100 customers from a single source. Not required. The annual report requirement in this Section does not apply to a master meter system, a petroleum gas system that serves fewer than 100 customers from a single source, or an individual service line directly connected to a production pipeline or a gathering line other than a regulated gathering line as determined in § 507. [49 CFR 191.11(b)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:219 (April 1983), amended LR 10:511 (July 1984), LR 11:255 (March 1985), LR 30:1222 (June 2004), LR 38:111 (January 2012), LR.

§312.	Distribution Systems: Mechanical Fitting Failure Reports [49 CFR 191.12]

A.	Each mechanical fitting failure, as required by §3509 of this part, must be submitted on a Mechanical Fitting Failure Report Form PHMSA F- 7100.1-2. An operator must submit a mechanical fitting failure report for each mechanical fitting failure that occurs within a calendar year not later than March 15 of the following year (for example, all mechanical failure reports for calendar year 2011 must be submitted no later than March 15, 2012). Alternatively, an operator may elect to submit its reports throughout the year. In addition, an operator must also report this information to the State pipeline safety authority if a state has obtained regulatory authority over the operator's pipeline. [49 CFR 191.12]

Repealed

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 38:111 (January 2012), LR.

- §322.	National & Louisiana Registry of Operators 
[49 CFR 191.22]

- A.	OPID Request. Effective January 1, 2012, each operator of a gas pipeline, gas pipeline facility, UNGSF, LNG plant, or LNG facility must obtain from PHMSA an Operator Identification Number (OPID). An OPID is assigned to an operator for the pipeline, pipeline facility, or pipeline system for which the operator has primary responsibility. To obtain an OPID, an operator must submit an OPID Assignment Request DOT Form PHMSA F 1000.1 through the National Registry of Operators in accordance with §307. For intrastate facilities subject to the jurisdiction of the Office of Conservation, the operator must concurrently file an online OR-1 Submission (Operator Registration) for Pipeline Safety with the same name as the OPID request at http://www.sonris.com. Each operator must validate the OR-1 annually by January 1 each year. [49 CFR 191.22(a)]

- 1.	Each operator of a Master Meter or Special Class System must file an online OR-1 Submission (Operator Registration) for Pipeline Safety at http://www.sonris.com. Each Master Meter and Special Class System operator must validate the OR-1 annually by January 1 each year.

- B. – D.	…

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 38:112 (January 2012), amended LR 44:1032 (June 2018), LR 45:67 (January 2019), LR 46:1575 (November 2020), LR.

- Chapter 4.  Appendix A [49 CFR Part 191]

§401.	Appendix A to Subpart 2—Procedure for

Determining Reporting Threshold

I.	Property Damage Threshold Formula

A.	Each year after calendar year 2021, the

Administrator will publish a notice on

PHMSA’s website announcing the updates to

the property damage threshold criterion that

will take effect on July 1 of that year and will

remain in effect until the June 30 of the next

year. The property damage threshold used in

the definition of an Incident at §303 shall

be determined in accordance with the

following formula:

Where:

Tr is the revised damage threshold,

Tp is the previous damage threshold,

CPIr is the average Consumer Price Indices

for all Urban Consumers (CPI–U)

published by the Bureau of Labor

Statistics each month during the most

recent complete calendar year, and

CPIp is the average CPI–U for the calendar

year used to establish the previous

property damage criteria.

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR

Subpart 3.  Transportation of Natural Gas or Other Gas by Pipeline: Minimum Safety Standards [49 CFR Part 192]

- Chapter 4.  Appendix A [49 CFR Part 191]

- Chapter 5.  General 
[49 CFR Part 192 Subpart A]

§507.	What Documents are Incorporated by Reference Partly or Wholly in this Part? 
[49 CFR 192.7]

A.	This part prescribes standards, or portions thereof, incorporated by reference into this part with the approval of the Director of the Federal Register in 5 U.S.C. 552(a) and 1 CFR part 51. The materials listed in this section have the full force of law. To enforce any edition other than that specified in this section, PHMSA must publish a notice of change in the Federal Register. Certain material is incorporated by reference into this Subpart with the approval of the Director of the Federal Register under 5 U.S.C. 552(a) and 1 CFR part 51. The materials listed in this Section have the full force of law. All approved material is available for inspection at Office of Pipeline Safety, Pipeline and Hazardous Materials Safety Administration, 1200 New Jersey Avenue S.E., Washington, D.C. 20590, 202-366-4046 https://www.phmsa.dot.gov/pipeline/regs, and is available from the sources listed in the remaining Subsections of this Section. It is also available for inspection at the National Archives and Records Administration (NARA). For information on the availability of this material at NARA, email fedreg.legal@nara.gov or go to www.archives.gov/federalregister/cfr/ibr-locations.html. [49 CFR 192.7(a)]

A.1 – A.2   …

| Source and Name of Referenced Material | Approved for Title 43 Reference |
| --- | --- |
| B. American Petroleum Institute (API), 1220 L Street NW., Washington, DC 20005, phone: 202-682-8000, http://api.org/. American Petroleum Institute (API), 200 Massachusetts Ave N.W., Suite 1100, Washington, D.C. 20001, and phone: 202-682-8000, Web site: https://www.api.org/. |  |
| B.1 – B.8 … |  |
| 9. API Standard 1104, “Welding of Pipelines and Related Facilities,” 20th edition, October 2005, including errata/addendum (July 2007) and errata 2 (2008), (API Std 1104). API Standard 1104, “Welding of Pipelines and Related Facilities,” 20th edition, October 2005, including errata/addendum (July 2007) and errata 2 (2008), (API Std 1104), | §§1305.A; 1307.A; 1309.C; 1321.C;Item II, 5103. |
| B.10 – D.2 … |  |
| E. American Society for Testing and Materials (ASTM), 100 Barr Harbor Drive, PO Box C700, West Conshohocken, PA 19428, phone: (610) 832-9585, Web site: http://www.astm.org/. ASTM International (formerly American Society for Testing and Materials), 100 Barr Harbor Drive, PO Box C700, West Conshohocken, PA 19428, phone: (610) 832-9585, Web site: http://astm.org |  |
| E.1 – E.10 … |  |
| 11. ASTM D2513-12ae1, “Standard Specification for Polyethylene (PE) Gas Pressure Pipe, Tubing, and Fittings,” April 1, 2012, (ASTM D2513-12ae1). ASTM D2513-18a, “Standard Specification for Polyethylene (PE) Gas Pressure Pipe, Tubing, and Fittings,” approved August 1, 2018, (ASTM D2513), | §5103, Item 1 |
| E.12 – E.19 … |  |
| 20. ASTM F2620-12, “Standard Practice for Heat Fusion Joining of Polyethylene Pipe and Fittings,” Aug. 1, 2012, (ASTM F2620-12). ASTM F2620-19, “Standard Practice for Heat Fusion Joining of Polyethylene Pipe and Fittings,” approved February 1, 2019, (ASTM F2620), | §§1511.C; 1515.B |
| E.21 – K.2 … |  |

- Chapter 9.  Pipe Design [49 CFR Part 192 Subpart C]

§921.	Design of Plastic Pipe [49 CFR 192.121]

A.	Design Formula Pressure. The design formulas pressure for plastic pipe are is determined in accordance with either of the following formulas.

where:

P = Design pressure, gauge, psig (kPa)

S = For thermoplastic pipe, the HDB is determined in accordance with the listed specification at a temperature equal to 73 ºF (23ºC), 100ºF (38ºC), 120ºF (49ºC), or 140ºF (60ºC). In the absence of an HDB established at the specified temperature, the HDB of a higher temperature may be used in determining a design pressure rating at the specified temperature by arithmetic interpolation using the procedure in Part D.2 of PPI TR-3/2012, HDB/PDB/SDB/MRS Policies”, (incorporated by reference, see §507). For reinforced thermosetting plastic pipe, 11,000 psig (75,842 kPa).

t = Specified wall thickness, in. (mm)

D = Specified outside diameter, in (mm)

SDR = Standard dimension ratio, the ratio of the average specified outside diameter to the minimum specified wall thickness, corresponding to a value from a common numbering system that was derived from the American National Standards Institute preferred number series 10.

DF = Design Factor, a maximum of 0.32 unless otherwise specified for a particular material in this Section. [49 CFR 192.121(a)]

B. – C.1.c  …

2.	For PE pipe produced on or after January 22, 2019, a DF of 0.40 may be used in the design formula, provided: [49 CFR 192.121(c)(2)]

C.2.a. – C.2.b.   …

c.	the pipe has a nominal size (IPS or CTS) of 1224 inches or less; and [49 CFR 192.121(c)(2)(iii)]

d.	the wall thickness for a given outside diameter is not less than that listed in Table 1 to this Subparagraph C.2.d the following table: [49 CFR 192.121(c)(2)(iv)]

| Table 1 to Subparagraph C.2.d PE Pipe: Minimum Wall Thickness and SDR Values |  |  |
| --- | --- | --- |
| Pipe Size (inches) | Minimum Wall Thickness | Corresponding SDR (values) |
| 1/2” CTS | 0.090 | 7 |
| 1/2” IPS | 0.090 | 9.3 |
| 3/4” CTS | 0.090 | 9.7 |
| 3/4” IPS | 0.095 | 11 |
| 1” CTS | 0.119 | 11 |
| 1” IPS | 0.119 | 11 |
| 1 1/4” IPS | 0.151 | 11 |
| 1 1/2” IPS | 0.173 | 11 |
| 2” | 0.216 | 11 |
| 3” | 0.259 | 13.5 |
| 4” | 0.265 | 17 |
| 6” | 0.315 | 21 |
| 8” | 0.411 | 21 |
| 10” | 0.512 | 21 |
| 12” | 0.607 | 21 |
| 16 | .762 | 21 |
| 18 | .857 | 21 |
| 20 | .952 | 21 |
| 22 | 1.048 | 21 |
| 24 | 1.143 | 21 |

D. – D.2.c.   …

d.	the minimum wall thickness for a given outside diameter is not less than that listed in Table 2 to Subparagraph D.2.d the following table. [49 CFR 192.121(d)(2)(iv)]

| Table 2 to Suparagraph D.2.d PE Pipe: Minimum Wall Thickness and SDR Values |  |  |
| --- | --- | --- |
| Pipe Size (inches) | Minimum Wall Thickness | Corresponding SDR (values) |
| 1/2” CTS | 0.090 | 7.0 |
| 1/2” IPS | 0.090 | 9.3 |
| 3/4” CTS | 0.090 | 9.7 |
| 3/4” IPS | 0.095 | 11 |
| 1” CTS | 0.119 | 11 |
| 1” IPS | 0.119 | 11 |
| 1 1/4 IPS | 0.151 | 11 |
| 1 1/2” IPS | 0.173 | 11 |
| 2” IPS | 0.216 | 11 |
| 3” IPS | 0.259 | 13.5 |
| 4” IPS | 0.333 | 13.5 |
| 6” IPS | 0.491 | 13.5 |

E. – E.1.c.   …

d.	the minimum wall thickness for a given outside diameter is not less than that listed in Table 3 to Subparagraph E.1.d  the following table. [49 CFR 192.121(e)(1)(iv)]

| Table 3 to Subparagraph E.1.d PE Pipe: Minimum Wall Thickness and SDR Values |  |  |
| --- | --- | --- |
| Pipe Size (inches) | Minimum Wall Thickness | Corresponding SDR (values) |
| 1/2” CTS | 0.090 | 7 |
| 1/2” IPS | 0.090 | 9.3 |
| 3/4” CTS | 0.090 | 9.7 |
| 3/4” IPS | 0.095 | 11 |
| 1” CTS | 0.119 | 11 |
| 1” IPS | 0.119 | 11 |
| 1 1/4” IPS | 0.151 | 11 |
| 1 1/2” IPS | 0.173 | 11 |
| 2” IPS | 0.216 | 11 |
| 3” IPS | 0.259 | 13.5 |
| 4” IPS | 0.333 | 13.5 |
| 6” IPS | 0.491 | 13.5 |

F. – F.2.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:222 (April 1983), amended LR 10:515 (July 1984), LR 24:1308 (July 1998), LR 27:1538 (September 2001), LR 30:1231 (June 2004), LR 31:682 (March 2005), LR 33:478 (March 2007), LR 35:2804 (December 2009), LR 38:115 (January 2012), repromulgated LR 38:828 (March 2012), amended LR 44:1037 (June 2018), LR 46:1582 (November 2020), LR.

- Chapter 11.  Design of Pipeline Components 
[49 CFR Part 192 Subpart D]

§1113.	Components Fabricated by Welding
[49 CFR 192.153]

A.	…

B.	Each prefabricated unit that uses plate and longitudinal seams must be designed, constructed, and tested in accordance with section 1 of the ASME BPVC (Section VIII, Division 1 or Section VIII, Division 2 Rules for Construction of Pressure Vessels as defined in either Section VIII, Division 1 or Section VIII, Division 2; incorporated by reference, see §507), except for the following: [49 CFR 192.153(b)]

B.1. – D.   …

E.	A component having a design pressure established in accordance with subsection A or Subsection B of this Section and subject to the strength testing requirements of §2305.B must be tested to at least 1.5 times the MAOP. The test requirements for a prefabricated unit or pressure vessel, defined for this Subsection as components with a design pressure established in accordance with Subsection A or Subsection B of this Section are as follows. [49 CFR 192.153(e)]

1.	prefabricated unit or pressure vessel installed after July 14, 2004 is not subject to the strength testing requirements at §2305.B provided the component has been tested in accordance with Subsection A or Subsection B of this Section and with a test factor of at least 1.3 times MAOP. [49 CFR 192.153(e)(1)]

2.	A prefabricated unit or pressure vessel must be tested for a duration specified as follows: [49 CFR 192.153(e)(2)]

a.	A prefabricated unit or pressure vessel installed after July 14, 2004, but before October 1, 2021 is exempt from §§2305.C and D and 2307.C provided it has been tested for a duration consistent with the ASME BPVC requirements referenced in Subsection A or B of this Section. [49 CFR 192.153(e)(2)(i)]

b.	Consider the information gained from past design, operations, and maintenance. [49 CFR 192.153(e)(2)(ii)]

3.	For any prefabricated unit or pressure vessel permanently or temporarily installed on a pipeline facility, an operator must either: [49 CFR 192.153(e)(3)]

a.	Test the prefabricated unit or pressure vessel in accordance with this Section and Chapter 23 of this Subpart after it has been placed on its support structure at its final installation location. The test may be performed before or after it has been tied-in to the pipeline. Test records that meet §2317.A must be kept for the operational life of the prefabricated unit or pressure vessel; or [49 CFR 192.153(e)(3)(i)]

b.	For a prefabricated unit or pressure vessel that is pressure tested prior to installation or where a manufacturer’s pressure test is used in accordance with Subsection E of this Section, inspect the prefabricated unit or pressure vessel after it has been placed on its support structure at its final installation location and confirm that the prefabricated unit or pressure vessel was not damaged during any prior operation, transportation, or installation into the pipeline. The inspection procedure and documented inspection must include visual inspection for vessel damage, including, at a minimum, inlets, outlets, and lifting locations. Injurious defects that are an integrity threat may include dents, gouges, bending, corrosion, and cracking. This inspection must be performed prior to operation but may be performed either before or after it has been tied-in to the pipeline. If injurious defects that are an integrity threat are found, the prefabricated unit or pressure vessel must be either non-destructively tested, re-pressure tested, or remediated in accordance with applicable Subpart 3(Part 192) requirements for a fabricated unit or with the applicable ASME BPVC requirements referenced in Subsections A or B of this Section. Test, inspection, and repair records for the fabricated unit or pressure vessel must be kept for the operational life of the component. Test records must meet the requirements in §2317.A. [49 CFR 192.153(e)(3)(ii)]

4.	An initial pressure test from the prefabricated unit or pressure vessel manufacturer may be used to meet the requirements of this Section with the following conditions: [49 CFR 192.153(e)(4)]

a.	The prefabricated unit or pressure vessel is newly-manufactured and installed on or after October 1, 2021, except as provided in Subparagraph E.4.b of this Section. [49 CFR 192.153(e)(4)(i)]

b.	An initial pressure test from the fabricated unit or pressure vessel manufacturer or other prior test of a new or existing prefabricated unit or pressure vessel may be used for a component that is temporarily installed in a pipeline facility in order to complete a testing, integrity assessment, repair, odorization, or emergency response-related task, including noise or pollution abatement. The temporary component must be promptly removed after that task is completed. If operational and environmental constraints require leaving a temporary prefabricated unit or pressure vessel under this Subsection in place for longer than 30 days, the operator must notify PHMSA and State or local pipeline safety authorities, as applicable, in accordance with § 518. [49 CFR 192.153(e)(4)(ii)]

c.	The manufacturer’s pressure test must meet the minimum requirements of this Subpart; and [49 CFR 192.153(e)(4)(iii)]

d.	The operator inspects and remediates the prefabricated unit or pressure vessel after installation in accordance with Subparagraph E.3.b of this Section. [49 CFR 192.153(e)(4)(iv)]

5.	An existing prefabricated unit or pressure vessel that is temporarily removed from a pipeline facility to complete a testing, integrity assessment, repair, odorization, or emergency response-related task, including noise or pollution abatement, and then re-installed at the same location must be inspected in accordance with Subparagraph E.3.b of this Section; however, a new pressure test is not required provided no damage or threats to the operational integrity of the prefabricated unit or pressure vessel were identified during the inspection and the MAOP of the pipeline is not increased. [49 CFR 192.153(e)(5)]

6.	Except as provided in Subparagraphs E.4.b and Paragraph E.5 of this Section, on or after October 1, 2021, an existing prefabricated unit or pressure vessel relocated and operated at a different location must meet the requirements of this Subpart and the following: [49 CFR 192.153(e)(6)]

a.	The prefabricated unit or pressure vessel must be designed and constructed in accordance with the requirements of this Subpart at the time the vessel is returned to operational service at the new location; and [49 CFR 192.153(e)(6)(i)]

b.	The prefabricated unit or pressure vessel must be pressure tested by the operator in accordance with the testing and inspection requirements of this Subpart applicable to newly installed prefabricated units and pressure vessels. [49 CFR 192.153(e)(6)(ii)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:223 (April 1983), amended LR 10:516 (July 1984), LR 20:444 (April 1994), LR 27:1539 (September 2001), LR 30:1234 (June 2004), LR 44:1037 (June 2018), LR.

- Chapter 13.  Welding of Steel in Pipelines [49 CFR Part 192 Subpart E]

1309.	Limitations on Welders [49 CFR 192.229]

A.	…

B.	No welder may weld with a particular welding process unless, within the preceding six calendar months, he has engaged in welding with that process. A welder or welding operator may not weld with a particular welding process unless, within the preceding 6 calendar months, the welder or welding operator was engaged in welding with that process. Alternatively, welders or welding operators may demonstrate they have engaged in a specific welding process if they have performed a weld with that process that was tested and found acceptable under section 6, 9, 12, or Appendix A of API Std 1104 (incorporated by reference, see §507) within the preceding 7 ½ months. [49 CFR 192.229(b)]

C. – D.2.b. …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:229 (April 1983), amended LR 10:521 (July 1984), LR 24:1309 (July 1998), LR 27:1541 (September 2001), LR 30:1241 (June 2004), LR 31:683 (March 2005), LR 33:479 (March 2007), LR 44:1038 (June 2018), LR.

- Chapter 15.  Joining of Materials Other Than by Welding 
[49 CFR Part 192 Subpart F]

§1511.	Plastic Pipe [49 CFR 192.281]

A.	- B.3.  …

C.	Heat-Fusion Joints. Each heat-fusion joint on a PE pipe or component, except for electrofusion joints, must comply with ASTM F2620-12 (incorporated by reference in §507), or an alternative written procedure that has been demonstrated to provide an equivalent or superior level of safety and has been proven by test or experience to produce strong gastight joints, and the following. [49 CFR 192.281(c)]

C.1 – E.4.  …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:231 (April 1983), amended LR 10:523 (July 1984), LR 20:445 (April 1994), LR 24:1309 (July 1998), LR 30:1243 (June 2004), LR 38:116 (January 2012), LR 44:1039 (June 2018), LR 46:1585 (November 2020), LR.

§1513.	Plastic Pipe: Qualifying Joining Procedures 
[49 CFR 192.283]

A. – A.2.   …

3.	for procedures intended for non-lateral pipe connections, perform testing in accordance with a listed specification. If the test specimen elongates no more less than 25 percent or failure initiates outside the joint area, the procedure qualifies for use. [49 CFR 192.283(a)(3)].

B. – D.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:231 (April 1983), amended LR 10:523 (July 1984), LR 20:445 (April 1994), LR 24:1310 (July 1998), LR 27:1541 (September 2001), LR 30:1244 (June 2004), LR 31:683 (March 2005), LR 33:479 (March 2007), LR 38:116 (January 2012), LR 44:1039 (June 2018), LR 46:1585 (November 2020), LR.

§1515.	Plastic Pipe: Qualifying Persons to Make Joints [49 CFR 192.285]

A. – B.2.   …

a.	tested under any one of the test methods listed under §1513.A, or and for PE heat fusion joints (except for electrofusion joints) visually inspected and tested in accordance with ASTM F2620-12 (incorporated by reference, see §507) or a written procedure that has been demonstrated to provide an equivalent or superior level of safety, applicable to the type of joint and material being tested; [49 CFR 192.285(b)(2)(i)]

B.2.b. – E.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:231 (April 1983), amended LR 10:524 (July 1984), LR 30:1244 (June 2004), LR 33:480 (March 2007), LR 44:1039 (June 2018), LR 46:1586 (November 2020), LR.

- Chapter 17.  General Construction Requirements for Transmission Lines and Mains 
[49 CFR Part 192 Subpart G]

§1725.	Installation of Plastic Pipelines By Trenchless Excavation [49 CFR 192.329]Underground Clearance [49 CFR 192.325]

A.	Plastic pipelines installed by trenchless excavation must comply with the following. [49 CFR 192.329]

1.	Each operator must take practicable steps to provide sufficient clearance for installation and maintenance activities from other underground utilities and/or structures at the time of installation. [49 CFR 192.329(a)]

2.	For each pipeline section, plastic pipe and components that are pulled through the ground must use a weak link, as defined by § 503, to ensure the pipeline will not be damaged by any excessive forces during the pulling process. [49 CFR 192.329(b)]

A.	Each transmission line must be installed with at least 12 inches (305 millimeters) of clearance from any other underground structure not associated with the transmission line. If this clearance cannot be attained, the transmission line must be protected from damage that might result from the proximity of the other structure. [49 CFR 192.325(a)]

B.	Each main must be installed with enough clearance from any other underground structure to allow proper maintenance and to protect against damage that might result from proximity to other structures. [49 CFR 192.325(b)]

C.	In addition to meeting the requirements of Subsections A or B of this Section, each plastic transmission line or main must be installed with sufficient clearance, or must be insulated, from any source of heat so as to prevent the heat from impairing the serviceability of the pipe. [49 CFR 192.325(c)]

D.	Each pipe-type or bottle type holder must be installed with a minimum clearance from any other holder as prescribed in §1135.B. [49 CFR 192.325(d)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:233 (April 1983), amended LR 10:525 (July 1984), LR 20:446 (April 1994), LR 27:1542 (September 2001), LR 30:1247 (June 2004), LR.

§1729.	Installation of Plastic Pipelines By Trenchless Excavation 
[49 CFR 192.329]

A.	Plastic pipelines installed by trenchless excavation must comply with the following. [49 CFR 192.329]

1.	Each operator must take practicable steps to provide sufficient clearance for installation and maintenance activities from other underground utilities and/or structures at the time of installation. [49 CFR 192.329(a)]

2.	For each pipeline section, plastic pipe and components that are pulled through the ground must use a weak link, as defined by § 503, to ensure the pipeline will not be damaged by any excessive forces during the pulling process. [49 CFR 192.329(b)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR.

- Chapter 21.  Requirements for Corrosion Control 
[49 CFR Part 192 Subpart I]

§2117.	External Corrosion Control: Monitoring 
[49 CFR 192.465]

A.	…

B.	Each cathodic protection rectifier or other impressed current power source must be inspected six times each calendar year, but with intervals not exceeding two and 
one-half months, to insure that it is operating. Cathodic protection rectifiers and impressed current power sources must be periodically inspected as follows:  [49 CFR 192.465(b)]

1.	Each cathodic protection rectifier or impressed current power source must be inspected six times each calendar year, but with intervals not exceeding 2 ½ months between inspections, to ensure adequate amperage and voltage levels needed to provide cathodic protection are maintained. This may be done either through remote measurement or through an onsite inspection of the rectifier. [49 CFR 192.465(b)(1)]

2.	After January 1, 2022, each remotely inspected rectifier must be physically inspected for continued safe and reliable operation at least once each calendar year, but with intervals not exceeding 15 months. [49 CFR 192.465(b)(2)]

C. – E.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:236 (April 1983), amended LR 10:528 (July 1984), LR 27:1545 (September 2001), LR 30:1253 (June 2004), LR 38:116 (January 2012), LR.

§2133.	Atmospheric Corrosion Control: Monitoring
[49 CFR 192.481]

A.	Each operator must inspect each pipeline or portion of pipeline that is exposed to the atmosphere for evidence of atmospheric corrosion, as follows. [49 CFR 192.481(a)]

| If the pipeline is located: | Then the frequency of inspection is: |
| --- | --- |
| Onshore other than a service line | At least once every 3 calendar years, but with intervals not exceeding 39 months. |
| Onshore service line | At least once every 5 calendar years, but with intervals not exceeding 63 months, except as provided in Subsection D of this Section. |
| Offshore | At least once each calendar year, but with intervals not exceeding 15 months. |

B. – C.   …

D.	If atmospheric corrosion is found on a service line during the most recent inspection, then the next inspection of that pipeline or portion of pipeline must be within 3 calendar years, but with intervals not exceeding 39 months. [49 CFR 192.481(d)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:237 (April 1983), amended LR 10:529 (July 1984), LR 30:1255 (June 2004), LR.

§2143.	Corrosion Control Records [49 CFR 192.491]

A. – B.   …

C.	Each operator shall maintain a record of each test, survey, or inspection required by this Section in sufficient detail to demonstrate the adequacy of corrosion control measures or that a corrosive condition does not exist. These records must be retained for at least five years, except that records related to §2117.A and E and §2127.B must be retained for as long as the pipeline remains in service. with the following exceptions: [49 CFR 192.491(c)]

1.	Operators must retain records related to §§ 2117.A and E and 2127.B for as long as the pipeline remains in service. [49 CFR 192.491(c)(1)]

2.	Operators must retain records of the two most recent atmospheric corrosion inspections for each distribution service line that is being inspected under the interval in §2133.A. [49 CFR 192.491(c)(2)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:237 (April 1983), amended LR 10:530 (July 1984), LR 24:1311 (July 1998), LR 30:1256 (June 2004), LR.

- Chapter 23.  Test Requirements 
[49 CFR Part 192 Subpart J]

§2307.	Test Requirements for Pipelines to Operate at a Hoop Stress Less Than 30 Percent of SMYS and At or Above 100 psi (689 kPa) Gauge
[49 CFR 192.507]

A.	 - A.3.   …

4.	For fabricated units and short sections of pipe, for which a post installation test is impractical, a pre-installation hydrostatic pressure test must be conducted in accordance with the requirements of this Section. [49 CFR 192.507(d)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:238 (April 1983), amended LR 10:530 (July 1984), LR 27:1545 (September 2001), LR 30:1257 (June 2004), LR.

- Chapter 27.  Operations 
[49 CFR Part 192 Subpart L]

§2719.	What is the Maximum Allowable Operating Pressure for Steel or Plastic Pipelines? 
[49 CFR 192.619]

A. – A.2.a.   …

b.	for steel pipe operated at 100 psi (689 kPa) gage or more, the test pressure is divided by a factor determined in accordance with the following table to Subparagraph A.2.b. [49 CFR 192.619(a)(2)(ii)]

| Table 1 to Subparagraph A.2.b |  |  |  |  |
| --- | --- | --- | --- | --- |
| Factors1, Segment |  |  |  |  |
| Class Location | Installed before (Nov. 12, 1970) | Installed after (Nov. 11, 1970) and before July 1, 2020 | Installed on or after July 1, 2020 | Converted under CFR §192.14 |
| 1 | 1.1 | 1.1 | 1.25 | 1.25 |
| 2 | 1.25 | 1.25 | 1.25 | 1.25 |
| 3 | 1.4 | 1.5 | 1.5 | 1.5 |
| 4 | 1.4 | 1.5 | 1.5 | 1.5 |

1For offshore segments installed, uprated or converted after July 31, 1977, that are not located on an offshore platform, the factor is 1.25. For segments installed, uprated or converted after July 31, 1977, that are located on an offshore platform or on a platform in inland navigable waters, including a pipe riser, the factor is 1.5.

2For a component with a design pressure established in accordance with §1113.A or B installed after July 14, 2004, the factor is 1.3.

A.3. – F.3.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 9:242 (April 1983), amended LR 10:534 (July 1984), LR 24:1312 (July 1998), LR 27:1547 (September 2001), LR 30:1264 (June 2004), LR 33:481 (March 2007), LR 35:2807 (December 2009), LR 46:1590 (November 2020), LR.

- Chapter 29.  Maintenance 
[49 CFR Part 192 Subpart M]

- §2912.	Analysis of Predicted Failure Pressure
[49 CFR 192.712]

- A.	 - E.2.a.iii   …

- (d).	if the pipeline segment has a history of reportable incidents caused by cracking or crack-like defects, maximum Charpy v-notch toughness values of 5.0 ft.-lbs. for body cracks and 1.0 ft.-lbs. for cold weld, lack of fusion, and selective seam w43	eld corrosion; or [49 CFR 192.712(de)(2)(i)(D)]

- (e).	other appropriate values that an operator demonstrates can provide conservative Charpy v-notch toughness values of crack-related conditions of the pipeline segment. Operators using an assumed Charpy v-notch toughness value must notify PHMSA in advance in accordance with § 518 and include in the notification the bases for demonstrating that the Charpy v-notch toughness values proposed are appropriate and conservative for use in analysis of crack-related conditions. [49 CFR 192.712(de)(2)(i)(E)]

- E.2.b – G.19.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 46:1595 (November 2020), LR.

§2940	Pressure Regulating, Limiting, and Overpressure Protection—Individual Service Lines Directly Connected to Regulated Gathering or  Production, Gathering, or Transmission Pipelines 
[49 CFR 192.740]

A.	This Section applies, except as provided in Subsection C of this Section, to any service line directly connected to a production, gathering, or transmission pipeline or regulated gathering pipeline as determined in § 507 that is not operated as part of a distribution system. [49 CFR 192.740(a)]

B. – B.4.   …

C.	This Section does not apply to equipment installed on service lines that only serve engines that power irrigation pumps. [49 CFR 192.740(c)]

1.	A service line that only serves engines that power irrigation pumps; [49 CFR 192.740(c)(1)]

2.	A service line included in a distribution integrity management plan meeting the requirements of Chapter 35 of this Subpart; or [49 CFR 192.740(c)(2)]

3.	A service line directly connected to either a production or gathering pipeline other than a regulated gathering line as determined in §508 of this Subpart. [49 CFR 192.740(c)(3)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, Pipeline Division, LR 44:1042 (June 2018), LR 46:1597 (November 2020), LR.

- Chapter 35.	Gas Distribution Pipeline Integrity Management (IM) 
[49 CFR Part 192 Subpart P]

§3503.	What do the Regulations in this Chapter Cover?	[49 CFR 192.1003]

A.	General. Unless exempted in Subsection B of this Section this Chapter prescribes minimum requirements for an IM program for any gas distribution pipeline covered under this Subpart, including liquefied petroleum gas systems. A gas distribution operator, other than a master meter operator or a small LPG operator, must follow the requirements in §§3505-3513 of this Chapter. A master meter operator or small LPG operator of a gas distribution pipeline must follow the requirements in §3515 of this Chapter. [49 CFR 192.1003(a)]

B.	Exceptions. This subpart does not apply to: an individual service line directly connected to a transmission, gathering, or production pipeline. [49 CFR 192.1003(b)

1.	Individual service lines directly connected to a production line or a gathering line other than a regulated onshore gathering line as determined in § 507; [49 CFR 192.1003(b)(1)]

2.	Individual service lines directly connected to either a transmission or regulated gathering pipeline and maintained in accordance with §2940.A and B; and [49 CFR 192.1003(b)(2)]

3.	Master meter systems. [49 CFR 192.1003(b)(3)]

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 38:123 (January 2012), amended LR 44:1044 (June 2018), LR.

§3505.	What must a Gas Distribution Operator (other than a master meter or Small LPG Operator) do to Implement this Chapter? [49 CFR 192.1005]

A.	…

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 38:123 (January 2012).

§3507.	What are the Required Elements of an Integrity Management Plan? [49 CFR 192.1007]

A. – A.1.e.   …

2.	Identify Threats. The operator must consider the following categories of threats to each gas distribution pipeline: corrosion (including atmospheric corrosion), natural forces, excavation damage, other outside force damage, material, or welds, equipment failure, incorrect operations, and other concerns that could threaten the integrity of its pipeline. An operator must consider reasonably available information to identify existing and potential threats. Sources of data may include, but are not limited to, incident and leak history, corrosion control records, continuing surveillance records, patrolling records, maintenance history, and excavation damage experience. [49 CFR 192.1007(b)]

A.3. – A.7.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 38:123 (January 2012), LR.

§3509.	What must an operator report when compression couplings fail? [49 CFR 192.1009]

A.	Except as provided in Subsection B of this Section, each operator of a distribution pipeline system must submit a report on each mechanical fitting failure, excluding any failure that results only in a nonhazardous leak, on a Department of Transportation Form PHMSA F-7100.1-2. The report(s) must be submitted in accordance with §312 of this Part. [49 CFR 192.1009(a)]

B.	The mechanical fitting failure reporting requirements in Subsection A of this Section do not apply to the following: [49 CFR 192.1009(b)]

1.	master meter operators; [49 CFR 192.1009(b)(1)]

2.	small LPG operator as defined in §3501; or [49 CFR 192.1009(b)(2)]

3.	LNG facilities. [49 CFR 192.1009(b)(3)]

Repealed

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 38:124 (January 2012), LR.

§3515.	What must a master meter or Small liquefied petroleum gas (LPG) Operator do to Implement this Chapter?	[49 CFR 192.1015]

A.	General. No later than August 2, 2011 the operator of a master meter system or a small LPG operator must develop and implement an IM program that includes a written IM plan as specified in Subsection B of this Section. The IM program for these pipelines should reflect the relative simplicity of these types of pipelines. [49 CFR 192.1015(a)]

B. – C.3.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, LR 38:124 (January 2012), LR.

Chapter 51.	Appendices

§5103.	Appendix B―Qualification of Pipe

I.	Listed Pipe Specifications

A.	Listed Pipe Specifications

1.  API Spec 5L—Steel pipe, “API Specification for Line Pipe” (incorporated by reference, see § 507).

2.  ASTM A53/A53M—Steel pipe, “Standard Specification for Pipe, Steel Black and Hot-Dipped, Zinc-Coated, Welded and Seamless” (incorporated by reference, see § 507).

3. ASTM A106/A-106M—Steel pipe, “Standard Specification for Seamless Carbon Steel Pipe for High Temperature Service” (incorporated by reference, see § 507).

4. ASTM A333/A333M—Steel pipe, “Standard Specification for Seamless and Welded Steel Pipe for Low Temperature Service” (incorporated by reference, see § 507).

5.	ASTM A381—Steel pipe, “Standard Specification for Metal-Arc-Welded Steel Pipe for Use with High-Pressure Transmission Systems” (incorporated by reference, see § 507).

6.	ASTM A671/A671M—Steel pipe, “Standard Specification for Electric-Fusion- Welded Pipe for Atmospheric and Lower Temperatures” (incorporated by reference, see § 507).

7.	ASTM A672/A672M-09—Steel pipe, “Standard Specification for Electric-Fusion- Welded Steel Pipe for High-Pressure Service at Moderate Temperatures” (incorporated by reference, see § 507).

8.	ASTM A691/A691M-09—Steel pipe, “Standard Specification for Carbon and Alloy Steel Pipe, Electric-Fusion-Welded for High Pressure Service at High Temperatures” (incorporated by reference, see § 507).

9.	ASTM D2513-12ae1“Standard Specification for Polyethylene (PE) Gas Pressure Pipe, Tubing, and Fittings” (incorporated by reference, see § 507).

10.	ASTM D 2517-00—Thermosetting plastic pipe and tubing, “Standard Specification for Reinforced Epoxy Resin Gas Pressure Pipe and Fittings” (incorporated by reference, see § 507).

11.	ASTM F2785-12 “Standard Specification for Polyamide 12 Gas Pressure Pipe, Tubing, and Fittings” (PA-12) (incorporated by reference, see § 507).

12.	ASTM F2817-10 “Standard Specification for Poly (Vinyl Chloride) (PVC) Gas Pressure Pipe and Fittings for Maintenance or Repair” (incorporated by reference, see § 507).

13.	ASTM F2945-12a “Standard Specification for Polyamide 11 Gas Pressure Pipe, Tubing, and Fittings” (PA-11) (incorporated by reference, see § 507).

B.	Other Listed Specifications for Components

1.	ASME B16.40-2008 “Manually Operated Thermoplastic Gas Shutoffs and Valves in Gas Distribution Systems” (incorporated by reference, see § 507).

2.	ASTM D2513-12ae1“Standard Specification for Polyethylene (PE) Gas Pressure Pipe, Tubing, and Fittings” (incorporated by reference, see § 507).

3.	ASTM D 2517-00—Thermosetting plastic pipe and tubing, “Standard Specification for Reinforced Epoxy Resin Gas Pressure Pipe and Fittings” (incorporated by reference, see § 507).

4.	ASTM F2785-12 “Standard Specification for Polyamide 12 Gas Pressure Pipe, Tubing, and Fittings” (PA-12) (incorporated by reference, see § 507).

5.	ASTM F2945-12a “Standard Specification for Polyamide 11 Gas Pressure Pipe, Tubing, and Fittings” (PA-11) (incorporated by reference, see § 507).

6.	ASTM F1055-98 (2006) “Standard Specification for Electrofusion Type Polyethylene Fittings for Outside Diameter Controlled Polyethylene Pipe and Tubing” (incorporated by reference, see § 507).

7.	ASTM F1924-12 “Standard Specification for Plastic Mechanical Fittings for Use on Outside Diameter Controlled Polyethylene Gas Distribution Pipe and Tubing” (incorporated by reference, see § 507).

8.	ASTM F1948-12 “Standard Specification for Metallic Mechanical Fittings for Use on Outside Diameter Controlled Thermoplastic Gas Distribution Pipe and Tubing” (incorporated by reference, see § 507).

9.	ASTM F1973-13 “Standard Specification for Factory Assembled Anodeless Risers and Transition Fittings in Polyethylene (PE) and Polyamide 11 (PA 11) and Polyamide 12 (PA 12) Fuel Gas Distribution Systems” (incorporated by reference, see § 507).

10.	ASTM F 2600-09 “Standard Specification for Electrofusion Type Polyamide-11 Fittings for Outside Diameter Controlled Polyamide-11 Pipe and Tubing” (incorporated by reference, see § 507).

11.	ASTM F2145-13 “Standard Specification for Polyamide 11 (PA 11) and Polyamide 12 (PA12) Mechanical Fittings for Use on Outside Diameter Controlled Polyamide 11 and Polyamide 12 Pipe and Tubing” (incorporated by reference, see § 507).

12.	ASTM F2767-12 “Specification for Electrofusion Type Polyamide-12 Fittings for Outside Diameter Controlled Polyamide-12 Pipe and Tubing for Gas Distribution” (incorporated by reference, see §507).

13.	ASTM F2817-10 “Standard Specification for Poly (Vinyl Chloride) (PVC) Gas Pressure Pipe and Fittings for Maintenance or Repair” (incorporated by reference, see §507).

II.	Steel Pipe of Unknown or Unlisted Specification

A.	Bending properties. For pipe 2 inches (51 millimeters) or less in diameter, a length of pipe must be cold bent through at least 90 degrees around a cylindrical mandrel that has a diameter 12 times the diameter of the pipe, without developing cracks at any portion and without opening the longitudinal weld.

For pipe more than 2 inches (51 millimeters) in diameter, the pipe must meet the requirements of the flattening tests set forth in ASTM A53, except that the number of tests must be at least equal to the minimum required in Paragraph II.D of this appendix to determine yield strength.

B.	Weldability. A girth weld must be made in the pipe by a welder who is qualified under Chapter 13 of this Subpart. The weld must be made under the most severe conditions under which welding will be allowed in the field and by means of the same procedure that will be used in the field. On pipe more than 4 inches (102 millimeters) in diameter, at least one test weld must be made for each 100 lengths of pipe. On pipe 4 inches (102 millimeters) or less in diameter, at least one test weld must be made for each 400 lengths of pipe. The weld must be tested in accordance with API Standard 1104 (incorporated by reference, see §507). If the requirements of API Standard 1104 cannot be met, weldability may be established by making chemical tests for carbon and manganese, and proceeding in accordance with Section IX of the ASME Boiler and Pressure Vessel Code (IBR, see §507). The same number of chemical tests must be made as are required for testing a girth weld.

C.	Inspection. The pipe must be cleaned enough to permit adequate inspection. It must be visually inspected to ensure that it is reasonably round and straight and there are no defects which might impair the strength or tightness of the pipe.

D.	Tensile properties. If the tensile properties of the pipe are not known, the minimum yield strength may be taken as 24,000 p.s.i. (165 MPa) or less, or the tensile properties may be established by performing tensile test as set forth in API Specification 5L (incorporated by reference, see §507).

| Number of Tensile Tests-All Sizes |  |
| --- | --- |
| 10 lengths or less | 1 set of tests for each length. |
| 11 to 100 lengths | 1 set of tests for each 5 lengths, but not less than 10 tests. |
| Over 100 lengths | 1 set of tests for each 10 lengths, but not less than 20 tests. |

If the yield-tensile ratio, based on the properties determined by those tests, exceeds 0.85, the pipe may be used only as provided in §705.C5(c).

III. – III.C.2.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, Pipeline Division, LR 10:541 (July 1984), amended LR 18:859 (August 1992), LR 27:1551, 1552 (September 2001), LR 30:1287 (June 2004), LR 31:689 (March 2005), LR 33:487 (March 2007), LR 35:2813 (December 2009), amended by the Department of Natural Resources, Office of Conservation, LR 38:125 (January 2012), LR 44:1045 (June 2018), LR 46:1601 (November 2020), LR.

Subpart 4.  Drug and Alcohol Testing

Chapter 61.  General [Part 199―Subpart A]

§6103.	Definitions [49 CFR 199.3]

* * *

Prohibited Drug―any of the following substances specified in Schedule I or Schedule II of the Controlled Substances Act, (21 U.S.C. §812) marijuana, cocaine, opiates, amphetamines, and phencyclidine (PCP) any of the substances specified in 49 CFR part 40.

* * *

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:751-757, redesignated as R.S. 30:701-707 and R.S. 30:501 et seq.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, Pipeline Division, LR 16:134 (February 1990), repromulgated LR 16:533 (June 1990), amended LR 18:852 (August 1992), LR 21:826, 829 (August 1995), LR 24:1306 (July 1998), LR 27:1554 (September 2001), LR 30:1292 (June 2004), LR 33:488 (March 2007), LR.

Title 33

ENVIRONMENTAL QUALITY

Part V.  Hazardous Wastes and Hazardous Materials

Subpart 3.  Natural Resources

- Chapter 304.	Transportation of Hazardous Liquids by Pipeline―Operation and Maintenance [49 CFR Part 195 Subpart F]

- §30416.	Inspections of Pipelines in Areas Affected by Extreme Weather and Natural Disasters Pipeline Assessments 
[49 CFR 195.416]

- A. – H.   …

AUTHORITY NOTE:	Promulgated in accordance with R.S. 30:753.

HISTORICAL NOTE:	Promulgated by the Department of Natural Resources, Office of Conservation, Pipeline Division, LR 46:1607 (November 2020), LR.

Family Impact Statement

- This Rule has no known impact on family formation, stability, and autonomy as described in R.S. 49:972.

Poverty Impact Statement

- This Rule has no known impact on poverty as described in R.S. 49:973.

Small Business Analysis

- This Rule has no known impact on small businesses as described in R.S. 49:965.6.

Provider Impact Statement

- This Rule has no known impact on providers as described in HCR 170 of 2014.

Public Comments

- All interested parties will be afforded the opportunity to submit data, views, or arguments, in writing. Written comments will be accepted by hand delivery or USPS only, until 4 p.m., June 21, 2020, at Office of Conservation, Pipeline Division, P.O. Box 94275, Baton Rouge, LA 70804-9275; or Office of Conservation, Pipeline Division, 617 North Third Street, Room 931, Baton Rouge, LA 70802. Reference Docket No. PRA 2021-01. All inquiries should be directed to Michael Peikert at the above addresses or by phone to (225) 219-3799. No preamble was prepared.

Richard P. Ieyoub

Commissioner